|  | ETP4830-A1 Engineer Manual |  |  |  |
| --- | --- | --- | --- | --- |
|  | Issue | 01 |  |  |
|  | Date | 2012-05-28 |  |  |
|  | HUAWEI TECHNOLOGIES CO., LTD. |  |  |  |

Copyright © Huawei Technologies Co., Ltd. 2012. All rights reserved. No part of this document may be reproduced or transmitted in any form or by any means without prior written consent of Huawei Technologies Co., Ltd. Trademarks and Permissions and other Huawei trademarks are trademarks of Huawei Technologies Co., Ltd. All other trademarks and trade names mentioned in this document are the property of their respective holders. Notice The purchased products, services and features are stipulated by the contract made between Huawei and the customer. All or part of the products, services and features described in this document may not be within the purchase scope or the usage scope. Unless otherwise specified in the contract, all statements, information, and recommendations in this document are provided "AS IS" without warranties, guarantees or representations of any kind, either express or implied. The information in this document is subject to change without notice. Every effort has been made in the preparation of this document to ensure accuracy of the contents, but all statements, information, and recommendations in this document do not constitute a warranty of any kind, express or implied.

| Huawei Technologies Co., Ltd. |  |
| --- | --- |
| Address: | Huawei Industrial Base Bantian, Longgang Shenzhen 518129 People's Republic of China |
| Website: | http://www.huawei.com |
| Email: | support@huawei.com |

About This Document

Purpose

This document describes the embedded telecom power 4830-A1 (ETP4830-A1) in terms of the composition, configurations, installation, cable connections, troubleshooting measures, and component replacement.

Intended Audience

This document is intended for:

Technical support personnel

Maintenance personnel

Symbol Conventions

The symbols that may be found in this document are defined as follows.

| Symbol | Description |
| --- | --- |
|  | Alerts you to a high risk hazard that could, if not avoided, result in serious injury or death. |
|  | Alerts you to a medium or low risk hazard that could, if not avoided, result in moderate or minor injury. |
|  | Alerts you to a potentially hazardous situation that could, if not avoided, result in equipment damage, data loss, performance deterioration, or unanticipated results. |
|  | Provides a tip that may help you solve a problem or save time. |
|  | Provides additional information to emphasize or supplement important points in the main text. |

Change History

Changes between document issues are cumulative. The latest document issue contains all the changes made in earlier issues.

Issue 01 (2012-05-28)

Contents

About This Document	ii

1 ETP4830-A1 Overview	1

1.1 System Composition and Configuration	1

1.2 Working Principles	1

1.3 Component Description	2

1.3.1 AC/DC Power Distribution Subrack	2

1.3.2 Rectifier	3

1.3.3 SMU	5

1.4 Monitoring Networking	6

1.5 Ports	6

2 Engineering Design	7

2.1 Engineering Drawing	7

2.2 Conceptual Diagram	8

3 Installation	9

3.1 Preparations	9

3.1.1 Getting Familiar with the Site	9

3.2 Installation	11

3.2.1 Installing a Power Subrack	11

3.2.2 Installing Modules	11

3.3 Cable Connections	12

3.3.1 Connecting Ground Cables	12

3.3.2 Connecting Communications Cables and Signal Cables	12

3.3.3 Connecting Load Cables	14

3.3.4 Connecting Battery Cables	14

3.3.5 Connecting AC Input Power Cables	14

3.4 Installation Verification and Power-On	15

3.5 Setting Parameters	15

4 Routine Maintenance	18

5 Troubleshooting	19

5.1 Troubleshooting Flowchart	19

5.2 Rectifying Common Faults	20

5.3 Component Troubleshooting	23

6 Component Replacement	25

7 Appendix	29

7.1 Technical Specifications	29

7.2 LCD Menu	32

A Acronyms and Abbreviations	33

ETP4830-A1 Overview

System Composition and Configuration

The ETP4830-A1 is a 1 U high embedded power system customized for access network equipment. It supplies stable and reliable direct current (DC) power to telecom equipment by converting alternating current (AC) into (DC).

System Composition

The ETP4830-A1 consists of a power distribution subrack, a site monitoring unit (SMU), and two rectifiers. Table 1-1 lists its components.

ETP4830-A1 components

| Power System | Component Model | Component | Quantity |
| --- | --- | --- | --- |
| ETP4830-A1 | ETP4830ZB-A1 | Power distribution subrack | 1 |
|  | SMU01B | SMU | 1 |
|  | R4815N1 | Rectifier | 2 |

ETP4830-A1

| (1) AC input port | (2) SMU01B | (3) R4815N1 (2 PCS) |
| --- | --- | --- |

Working Principles

The ETP4830-A1 working principles are described as follows:

The ETP4830-A1 is supplied with single-phase AC power.

Rectifiers are energized by AC power through a backplane.

The DCs generated by rectifiers converge on a busbar and then are divide into multiple routes to power loads.

The SMU monitors operating parameters for the ETP4830-A1 in real time, analyzes the operating status, and generates alarms when necessary.

ETP4830-A1 conceptual diagram

Component Description

AC/DC Power Distribution Subrack

AC/DC power distribution subrack of the ETP4830-A1

Cables are routed in and out from the front, which is easy to maintain and operate.

Rectifier

Rectifier

The rectifier has the following features:

Works efficiently and runs stably.

Is hot-swappable.

Is protected against input overvoltage, input undervoltage, input overcurrent, output overvoltage, output short circuit, output current limiting, and overtemperature.

For details about the rectifier technical specifications, see Table 2-1.

Rectifier panel

| (1) Power indicator | (2) Alarm indicator | (3) Fault indicator |
| --- | --- | --- |

Indicator description

| Indicator | Color | Status | Description | Measures |
| --- | --- | --- | --- | --- |
| Power indicator | Green | Steady on | The rectifier has an AC power input. | The rectifier runs properly and no measure is required. |
|  |  | Off | The rectifier has no AC power input. | Replace the rectifier if the AC input is normal. |
|  |  |  | The rectifier is faulty. | Replace the rectifier. |
|  |  | Blinking at 0.5 Hz | The rectifier is being queried. | The rectifier runs properly and no measure is required. |
|  |  | Blinking at 4 Hz | The rectifier is loading an application program. | The rectifier automatically recovers after loading, and no measure is required. |
| ALM indicator | Yellow | Off | No alarm is generated. | The rectifier runs properly and no measure is required. |
|  |  | Steady on | The rectifier generates a prewarning for power limiting due to ambient overtemperature. The rectifier generates an alarm for protection or shut-down due to ambient overtemperature or undertemperature. | Check that the air vent is not blocked and the ambient temperature is within a normal range. |
|  |  |  | The rectifier is protected against AC input overvoltage or undervoltage. | Check the power grid voltage. |
|  |  |  | The rectifier is hibernating. | The rectifier runs properly and no measure is required. |
|  |  | Blinking at 0.5 Hz | The rectifier communication is interrupted. | Replace the rectifier or SMU. |
| Fault indicator | Red | Off | The rectifier is not faulty. | The rectifier runs properly and no measure is required. |
|  |  | Steady on | The rectifier is locked due to output overvoltage. | Remove the rectifier and then insert it after 1 minute. |
|  |  |  | There is no output because the rectifier is faulty. | Replace the rectifier. |

SMU

SMU

The SMU performs the following functions:

Performs comprehensive power management and intelligent battery management.

Provides four dry contact outputs over the DB 50 port.

Provides seven reserved Boolean value inputs over the DB 50 port.

SMU panel

| (1) Run indicator | (2) Alarm indicator | (3) Liquid crystal display (LCD) |
| --- | --- | --- |
| (4) Button | (5) Locking latch | (6) DB50 port (reserved) |
| (7) Battery temperature sensor port | (8) RS232/RS485 port | (9) COM port |

Indicator description

| Power System | Color | Status | Description |
| --- | --- | --- | --- |
| Run indicator | Green | Off | The SMU is faulty or has no power input. |
|  |  | Blinking at 0.5 Hz | The SMU runs properly and communicates with the host properly. |
|  |  | Blinking at 4 Hz | The SMU runs properly but does not communicate with the host properly. |
| Fault indicator | Red | Off | No major alarm is generated. |
|  |  | Steady on | A major alarm is generated. |

Monitoring Networking

The ETP4830-A1 is networked with access network equipment through an SMU only over point to point (PTP) protocols, original master/slave protocols, and normalized master and slave protocols.

Ports

The ports on the ETP4830-A1 include the AC input port, AC output port, DC input port, and DC output port on the power distribution subrack, and the communications ports on the SMU. For details, see section 1.3 "Component Description."

Engineering Design

Engineering Drawing

ETP4830-A1 dimensions

Specifications for input and output terminals

| Terminal | Capacity | User Cable Terminal | Recommended Cable | Protection Fuse Capacity |
| --- | --- | --- | --- | --- |
| AC input terminal (L and N) | 13 A Max | OT4 wiring terminal | 2.5–4 mm2 |  |
| Protective earth (PE) | N/A | OT4 wiring terminal | 2.5–4 mm2 |  |
| Load 1 (LOAD1) | 17 A | 14120040x1 14110036x4 | Two 1 mm2 cables | 20 A (fuse) |
| Load 2 (LOAD2) | 17 A | 14120040x1 14110036x4 | Two 1 mm2 cables | 20 A (fuse) |
| Battery (BATT) | 17 A | 14120040x1 14110036x4 | Two 1 mm2 cables | 20 A (fuse) |
| NOTE The actual ampacity on each DC output route must be lower than or equal to the rated capacity of the fuse that controls the route. |  |  |  |  |

Conceptual Diagram

See Figure 1-2.

Installation

Preparations

Getting Familiar with the Site

The ETP41830-A1 applies to a standard 19-inch rack. For its dimensions, see section 2.1 "Engineering Drawing."

Project Survey

The ETP4830-A1 is a power system embedded in a cabinet, so its connections are mainly inside the cabinet, and the related cables are provided by the cabinet supplier.

Tools

Tools

| Tool | Picture | Function |
| --- | --- | --- |
| Multimeter |  | Used to measure electrical properties. |
| Phillips screwdriver (M3 and M6) |  | Used to connect cables and tighten screws. |
| Flat-head screwdriver (M3 and M6) |  | Used to connect cables and tighten screws. |
| Socket wrench |  | Used to tighten bolts |
| Torque wrench |  | Used to tighten bolts |
| Adjustable wrench |  | Used to tighten bolts |
| Hex key (M5) |  | Used to tighten bolts |
| COAX crimping tool |  | Used to crimp cord end terminals. |
| Diagonal pliers |  | Used to cut cables |
| Wire stripper |  | Used to peel cables |
| Polyvinyl chloride (PVC) insulation tape |  | Used to insulate wires and conductors. |
| Fuse extracting unit |  | Used to install or remove fuses. |
| Brush |  | Used to clean shells and panels and apply paint. |
| Sandpaper |  | Used to remove rust. |
| Cotton cloth |  | Used to clean shells and panels. |
| Protective gloves |  | Used to protect hands. |
| Paint |  | Used to prevent rust. |

Installation

Installing a Power Subrack

Figure 3-1 shows how to install an ETP4830-A1 in a 19-inch rack.

Rack-mounting an ETP4830-A1

Installing Modules

This section describes how to install an SMU and rectifiers.

After installing a module, push the locking latch towards the right to lock the module.

Installing an SMU

Installing an SMU

To install an SMU, perform the following steps:

          - Open the SMU handle and push the SMU into the correct slot shown in Figure 1-1.

Push the handle into the handle slot.

Push the locking latch towards the right to lock the SMU.

----End

Installing Rectifiers

A rectifier is installed in the same manner as an SMU.

Cable Connections

Connect cables in the following sequence: ground cables, communications cables, signal cables, load cables, battery cables, and AC input power cables.

Before connecting a cable, ensure that no AC power is being supplied.

Do not confuse load ports and battery ports.

Connecting Ground Cables

Ground cables must be connected first and disconnected last. Figure 3-3 shows how an ETP4830-A1 is grounded.

Ground cable connection

Connecting Communications Cables and Signal Cables

Connecting Communications Cables

Figure 3-4 shows how a communications cable is connected. Table 3-2 describes the communications ports.

Communications cable connection

Communications port description

| Communications Port | Communications Parameter | Protocol |
| --- | --- | --- |
| COM port | Baud rate: 9600 bit/s or 19,200 bit/s | Access network protocol |
| RS485/RS232 port | Baud rate: 9600 bit/s or 19,200 bit/s | Access network protocol |

Description for the pins in the COM and RS485/RS232 ports

| Pin | Signal | Description |
| --- | --- | --- |
| 1 | TX+ | Sends data over RS485. |
| 2 | TX– |  |
| 4 | RX+ | Receives data over RS485. |
| 5 | RX– |  |
| 3 | RX232 | Receives data over RS232. |
| 7 | TX232 | Sends data over RS232. |
| 6 | PGND | Connects to the ground. |
| 8 | N/A | N/A |

Connecting Load Cables

Load cable connection

Connecting Battery Cables

Battery cables are connected in the same manner as load cables.

Connecting AC Input Power Cables

Before connecting an AC input power cable, switch the corresponding circuit breaker on the alternating current distribution box (ACDB) to OFF.

Before connecting an AC input power cable, install an external circuit breaker to protect the ETP4830-A1.

To connect an AC input power cable to the ETP4830-A1, perform the following steps:

Remove the protective cover over AC input terminals.

Connect the neutral wire to the N wiring terminal.

Connect the live wire to the L wiring terminal.

If a 100/110 V dual-live wire is used, connect the two live wires to the L and N wiring terminals respectively.

AC input power cable connection

Installation Verification and Power-On

Verifying the Installation

After the installation, verify that:

The ETP4830-A1 is grounded properly.

All cables are connected securely.

The AC input circuit breaker is switched off.

Load cables and battery cables are connected correctly.

No short circuit occurs between live wires, neutral wires, and ground cables, between load polarities, or between battery polarities. If any short circuit occurs, check the cable connections carefully before powering on the ETP4830-A1.

Powering On the ETP4830-A1

To power on the ETP4830-A1, perform the following steps:

Switch on the AC input circuit breaker.

Connect rectifiers. If the Run indicator (green) on a rectifier panel is steady on, the rectifier is powered on successfully.

If the Run indicator (green) on the SMU panel is blinking and the LCD is on, the SMU is powered on successfully.

Setting Parameters

After powering on the ETP4830-A1 for the first time, set the SMU parameters based on the actual ETP4830-A1 configuration.

Set SMU communications parameters based on actual requirements.

To allow the SMU to communicate with Huawei communications equipment over an RS485/RS232 port, set communications addresses for Huawei communications equipment on the LCD.

Setting Parameters for the Communication with Huawei Communications Equipment

On the LCD, set the communications address (0 by default) by choosing Settings -> Com Settings -> Address and set baud rate (9,600 bit/s by default) by choosing Settings -> Com Settings -> COM Port -> Baud.

Setting System Parameters

After the ETP4830-A1 is delivered, certain parameters on the SMU are configured by default. You can change the parameter values on the LCD. Table 3-4 lists the configurable parameters.

Configurable parameters

| Second-Level Menu | Third-Level Menu | Fourth-Level Menu | Default Value | Value Range |
| --- | --- | --- | --- | --- |
| Batt Settings | Batt String | N/A | 1 | 0–1 |
|  | Capacity | N/A | 12 | 5AH–1000AH |
| Com Settings | Address | N/A | 0 | 0–31 |
|  | COM Port | Baud | 9600 | 9600, 19200 |
|  | RS485/RS232 Port | Baud | 9600 | 9600, 19200 |
|  |  | Mode Select | Slave | Slave, Master |
| DC Settings | FC Volt | N/A | 53.5V | 47.0V–57.5V |
|  | BC Volt | N/A | 56.5V | 53.6V–57.0V |
|  | Over Volt | N/A | 58.0V | 58.0V–60.0V |
|  | Under Volt | N/A | 45.0V | 44.1V–51.5V |
|  | LLVD Enable | N/A | No | No, Yes |
|  | LLVD Volt | N/A | 44.0 | 43.1-44.9 |
|  | BLVD Enable | N/A | Yes | Yes, No |
|  | BLVD | N/A | 43.0V | 35.0V-43.8V |
| AC Settings | Over Volt | N/A | 280VAC | 181VAC–300VAC |
|  | Under Volt | N/A | 180VAC | 60VAC–279VAC |
| Alarm Settings | Alarm Severity | N/A | N/A | N/A |
|  | Digital Alarm | N/A | N/A | N/A |
|  | Rely Relate | N/A | N/A | N/A |
| Rec Settings | Sleep Enable | N/A | No | Yes, No |
|  | Best Effi Point | N/A | 70% | 60%–80% |
|  | Exch Cycle | N/A | 7days | 5–30 days |
|  | Min Num Rect On | N/A | 1 psc | 1–3 PSC |
| System Settings | Text | N/A | Chinese | Chinese, English |
|  | Batt Shunt Coef | N/A | 50A/50mV | 1–999A/1–99mV |
|  | Disp Contrast | N/A | 3 | 2–5 |
|  | Modify PWD | N/A | 00200 | N/A |
|  |  | N/A | 10020 | N/A |
|  | Date | N/A | N/A | N/A |
|  | Time | N/A | N/A | N/A |

Routine Maintenance

Maintain the ETP4830-A1 periodically based on site requirements. The recommended maintenance period is six months. If any fault is detected, rectify it immediately.

Routine maintenance checklist

| Task | Content |  |  |  |
| --- | --- | --- | --- | --- |
|  | Check That | Check Method | Repair When | Measures |
| Preventive maintenance inspection (PMI) | Indicators are in the normal state. | Observe the indicators. | Alarms are generated. | See section 5.2 "Rectifying Common Faults." |

Troubleshooting

Troubleshooting Flowchart

Rectifying Common Faults

Common faults and troubleshooting measures

| Symptom | Possible Cause | Measures |
| --- | --- | --- |
| AC power failure | The AC input power cable is faulty. The mains supply or diesel generator (D.G.) fails. | - If the AC input power cable is not connected properly, reconnect it. - If the AC input power is unavailable, check that no open or short circuits occur in the AC input loop. If the AC input loop is normal, contact the mains supplier. If the AC input is from a D.G., check and repair the D.G. by referring to the D.G. User Manual. - If the power failure is for a short time, use storage batteries to power DC-powered loads. If the power failure is for a long time, use another power supply. |
| AC overvoltage or undervoltage | The AC overvoltage or undervoltage alarm threshold is not set properly on the SMU. The mains supply or D.G. fails. | - Adjust the AC overvoltage or undervoltage alarm threshold to a proper value. - If the AC input is from mains, contact the mains supplier. If the AC input is from a D.G., check and repair the D.G. by referring to the D.G. User Manual. |
| DC overvoltage or undervoltage | The DC overvoltage or undervoltage alarm threshold is not set properly on the SMU. The rectifier is faulty. | - Adjust the DC overvoltage or undervoltage alarm threshold to a proper value. - If storage batteries supply power properly, remove all rectifiers and then install them one by one. If an overvoltage alarm is generated when you install a rectifier, replace this rectifier. |
| Charge overcurrent | Rectifier communication failure The battery loop is faulty. | - Install the rectifier in the correct subrack. If the rectifier has poor contact with the subrack, reseat it and secure it to the subrack. - Check that the battery loop is not faulty or short-circuited. - Replace faulty storage batteries. |
| Battery disconnection. | The battery parameters are not set properly on the SMU. The contactor is faulty. | - If the mains supply fails or the battery voltage is below the BLVD threshold, contact the mains supplier. - Enable the BLVD function on the SMU. - Replace faulty battery cables and connectors. - If the contactor is faulty or cannot be connected or disconnected, replace the contactor. |
| Battery loop disconnection | The battery fuse is blown. The battery loop is faulty. The contactor is faulty. Storage batteries are faulty. | - Replace faulty fuses. - Replace faulty battery cables and connectors. - If the contactor is faulty or cannot be connected or disconnected, replace the contactor. - Replace faulty storage batteries. |
| Overhigh or over low ambient temperature This alarm can be generated only when an ambient temperature sensor is installed. | The ambient temperature alarm threshold is not properly set on the SMU. The temperature inside the shelter where the ambient temperature sensor is installed is beyond a normal range. The ambient temperature sensor is faulty. | - Adjust the ambient temperature alarm threshold to a proper value. - Repair the temperature control system in the shelter if it is faulty. After the temperature inside the shelter is adjusted to a normal range, the alarm is automatically cleared. - Replace the faulty ambient temperature sensor. |
| Overhigh or over low ambient humidity This alarm can be generated only when a humidity sensor is installed. | The ambient humidity alarm threshold is not properly set on the SMU. The shelter where the humidity sensor is installed is beyond a normal range. The humidity sensor is faulty. | - Adjust the ambient humidity alarm threshold to a proper value. - If there is water in the shelter, remove the water by using a dry cotton cloth or dehumidifier. - If the ambient humidity is within a normal range but the alarm persists, check and repair the humidity sensor. |
| Overhigh or over low battery temperature (This alarm can be generated only when a battery sensor is installed.) | Temperature inside the battery compartment is greater than the maximum value. The battery temperature alarm threshold is not properly set on the SMU. The battery charge current is greater than the maximum value. The battery temperature sensor is faulty. | - Adjust the battery temperature alarm threshold to a proper value. - If the temperature inside the battery compartment is greater than the maximum value, lower the temperature. The alarm is cleared automatically after the temperature drops to a normal range. - If the charge current is greater than the maximum value, change equalized charging into float charging and check whether the charge current is lowered. If the charge current is still overhigh, reduce the charge current. If the battery temperature is still greater than the maximum value, replace faulty storage batteries. - Replace the faulty battery temperature sensor. |
| Door status sensor alarm (This alarm can be generated only when a door status sensor is installed.) | The cabinet door is open. The door status sensor is faulty. | - Close the cabinet door. - If the alarm persists after the cabinet door is closed, check and repair the door status sensor. |
| Water sensor alarm (This alarm can be generated only when a water sensor is installed.) | There is water in the shelter. The water sensor is faulty. | - If there is water in the shelter, remove the water by using a dry cotton cloth or dehumidifier. - If there is no water but the alarm persists, check and repair the water sensor. |
| Smoke sensor alarm (This alarm can be generated only when a smoke sensor is installed.) | There is smoke in the shelter. The smoke sensor is faulty. | - If there is smoke in the shelter, put out the fire immediately and open the shelter door for ventilation. - If there is no smoke but the alarm persists, check and repair the smoke sensor. |
| Rectifier fault | The rectifier has poor contact with the monitoring backplane. The rectifier is faulty. | - If the Fault indicator on the rectifier panel is steady red, remove the rectifier, and then reinstall it after the indicator turns off. - If the alarm persists, replace the rectifier. |
| Rectifier shutdown Rectifier protection | The rectifier input voltage is beyond a normal range. The rectifier is faulty. | - If the mains supply voltage is higher than the rectifier AC overvoltage threshold (300 V) or lower than the rectifier AC undervoltage threshold (85 V) for a long time, contact the mains maintenance personnel to improve the power grid. - If the rectifier input voltage is within a normal range but the alarm persists, replace the rectifier. |
| Failed communication between the rectifier and the SMU | The rectifier has poor contact with the monitoring backplane. The rectifier is not installed. The rectifier is faulty. | - Install the rectifier in the correct subrack. If the rectifier has poor contact with the subrack, reseat it and secure it to the subrack. - If the alarm persists, replace the rectifier. |
| Load fuse blown | The load current is greater than the maximum value or the load route is short-circuited. | If the load power is within a normal range and the load route is not short-circuited, replace the fuse. |

After a fault is rectified, the corresponding alarm is automatically cleared on the SMU and the alarm information is stored in the alarm history.

After replacing an SMU, reset parameters.

The SMU and rectifiers are hot-swappable.

Component Troubleshooting

Rectifying Rectifier Faults

A rectifier is damaged if either of the following conditions is not met:

When the rectifier does not communicate with the SMU, the Run indicator on the rectifier is steady on, the Fault indicator is off, and the AC input voltage is around 220 V. The rectifier output is normal.

The SMU can perform equalized charging, float charging, and current limiting control for the rectifier when the communication cable to the rectifier is correctly connected and communication is established between the rectifier and the SMU.

Rectifying SMU Faults

The common SMU faults are as follows:

The SMU is faulty, for example, when one of the following occurs: SMU breakdown, startup failure, LCD failure, and keyboard operation failure.

The SMU does not generate an alarm when a fault occurs.

The SMU generates an alarm (false alarm) when the system runs properly.

Communication is interrupted when the SMU monitors the subordinate equipment.

The SMU fails to control or monitor all the modules when these modules run properly and communications cables are connected properly.

The SMU fails to monitor and control AC distribution and DC distribution when AC and DC power is distributed normally and communications cables are connected properly.

Parameters cannot be set or operating information cannot be viewed on the SMU.

Component Replacement

Do not disconnect loads when replacing main components. You must take measures to ensure that loads are not disconnected. For example, do not disconnect storage batteries or the AC input power at the same time.

If load disconnection is indeed required, seek the customer's prior consent.

Rectifiers and the SMU are hot-swappable.

Replacing a Rectifier

To replace a rectifier, perform the following steps:

Unscrew the rectifier panel using a screwdriver.

Gently draw the handle outwards, and then remove the rectifier from the subrack, as shown in Figure 6-1.

Insert a new rectifier into the subrack. Then loosen the screws on the handle and pull out the handle.

Slide the new rectifier into the subrack slowly along the guide rail, and then lock the handle.

Tighten the screws on the handle, as shown in Figure 6-2.

Removing a rectifier

Installing a rectifier

----End

Replacing an SMU

To replace an SMU, perform the following steps:

Push the locking latch towards the left.

Draw the handle outwards to remove the SMU, as shown in Figure 6-3.

Removing an SMU

Insert a new SMU into the subrack, push the locking latch towards the left, and pull out the handle.

Slide the new SMU into the subrack slowly along the guide rail, and then push the locking latch towards the right, as shown in Figure 6-4.

Resetting parameters on the SMU.

Installing an SMU

----End

Replacing a Power Distribution Subrack

To replace an SMU, perform the following steps:

Disconnect the power supply to the ETP4830-A1.

Remove the SMU and all rectifiers.

Disconnect the cables to the power distribution subrack and then remove the subrack.

Install a new subrack.

Reinstall the SMU and all rectifiers and reconnect the cables.

----End

Replacing a Fuse

Table 6-1 lists the specifications for the load and battery fuses. A new fuse must have the same specifications as the original fuse.

Fuse specifications

| Fuse | Specifications |
| --- | --- |
| (1) LOAD1 fuse | 250 V AC, 20 A, slow blowing |
| (2) LOAD2 fuse | 250 V AC, 20 A, slow blowing |
| (3) BATT fuse | 250 V AC, 20 A, slow blowing |

To replace a fuse, perform the following steps:

          - Disconnect the loads on the same route as the fuse.

Hold down the fuse holder and turn it anticlockwise, and then remove the fuse.

Insert a new fuse with the same specifications as the original one into the fuse holder. Hold down the fuse holder and turn it clockwise to install the fuse.

Connect the loads on the same route as the fuse.

Replacing a Battery String

To avoid system power failures, replace a battery string by performing the following steps:

Ensure that the AC input power supply is normal.

On the LCD, configure the ETP4830-A1 to work in manual mode and disconnect the BLVD route.

Remove the battery fuse.

Replace the storage batteries.

Reinstall the battery fuse.

Configure the ETP4830-A1 to work in automatic mode.

Wait until the ETP4830-A1 is powered on automatically.

You can leave the site only after checking that:

No battery loop broken alarm is generated.

The battery charge current is not 0.

----End

Appendix

Technical Specifications

Technical specifications

| Category | Item | Specifications |
| --- | --- | --- |
| Environmental specifications | Operating temperature | –40°C to +70°C |
|  | Storage temperature | –40°C to +70°C |
|  | Transportation temperature | –40°C to +70°C |
|  | Operating humidity | 5%–95% RH (non-condensing) |
|  | Storage humidity | 5%–95% RH (non-condensing) |
|  | Altitude | 0–4000 m When the altitude ranges from 2000 m to 4000 m, the operating temperature decreases by 1ºC for each additional 200 m. |
|  | Other requirements | The LCD is normal within the operating temperature range of –20°C to +70°C and the storage temperature range of –30°C to +80°C. |
| AC input | Input mode | Single-phase, three-wire (L, N, and PE) |
|  | Input voltage | 85–300 V AC (rated voltage: 220 V AC) |
|  | Input frequency | 45–66 Hz (rated frequency: 50 Hz) |
|  | Power factor | ≥ 0.99 (100% load power) |
| DC output | Output voltage range | –43.2 V to –57.6 V |
|  | Default output voltage | –53.5 V |
|  | Maximum output power | 2x1000 W |
|  | Regulated voltage precision | ≤ ±0.6% |
|  | Peak-to-peak noise voltage | ≤ 200 mV (0–20 MHz) |
|  | Others | No damage is caused if a storage battery is connected reversely. |
| AC input protection | AC input overvoltage protection threshold | Overvoltage protection is triggered when the single-phase AC input voltage exceeds the AC input overvoltage protection threshold (300 V AC by default). |
|  | AC input overvoltage recovery threshold | When the voltage is restored to 290 V AC, the output resumes. |
|  | AC input undervoltage protection threshold | Undervoltage protection is triggered when the single-phase AC input voltage is below the AC input undervoltage protection threshold (80 V AC by default). |
|  | AC input undervoltage recovery threshold | When the voltage is restored to 85 V AC, the output resumes. |
| DC output protection | DC output overvoltage protection threshold | 58.5–60.5 V DC |
| Rectifier | Efficiency | R4850N1: > 93% (30%–100% load power), maximum point: 94% |
|  | Output power | R4815N1: 1000 W (input voltage: 176–300 V AC) 500 W (input voltage: 85–175 V AC) |
|  | Overvoltage protection | Voltage range: 58.5–60.5 V DC If an overvoltage occurs inside the rectifier, the rectifier experiences a deadlock. External overvoltage: If the external voltage is less than 63 V, the rectifier is in the standby. If overvoltage disappears, the rectifier output resumes. If the external voltage is greater than 63 V for more than 500 ms, the rectifier experiences a deadlock. |
| EMC specifications | Conducted emission (CE)/Radiated emission (RE) | CISPR 22/EN 55022 class B |
|  | Harmonic | IEC 61000-3-12 |
|  | Fluctuation and blinking | IEC 61000-3-3 |
|  | Electrostatic discharge (ESD) | Contact discharge: 6 kV Air discharge: 8 kV Signal port discharge: 2 kV |
|  | Electrical fast transient (EFT) | Signal port: 1 kV (criterion B Power port: 2 kV (criterion B) |
|  | Radiated susceptibility (RS) | Signal port: 3 V/m Power port: 10 V/m |
|  | Conducted susceptibility (CS) | Signal port: 3 V Power port: 10 V |
|  | Surge | For AC power ports, Differential mode: 2 kV Common mode: 4 kV |
|  | DIP | IEC61000-4-11 |
| Others | Surge protection | For AC power ports, Differential mode: 5 kA Common mode: 5 kA |
|  | Safety and regulatory design | Complies with IEC 60950-1/GB 4943 and passes the certification of the Conformite Europeenne (CE) and Technical Watch-Over Association (TUV). |
|  | Mean time between failures (MTBF) | 250,000 hours (at 25°C) |
| Structure | Dimensions (H x W x D) | ETP4830-A1: 43.6 mm x 442 mm x 25 5 mm R4815N1 and SMU01B: 40.8 mm x 95.5 mm x 208 mm |
|  | Weight | ≤ 10 kg (including modules) |
|  | Protection level | IP20 |
|  | Installation mode | Installed in a 19-inch cabinet by being equipped with mounting ears |
|  | Maintenance mode | Operated and maintained from the front |
|  | Cooling mode | Fan-cooled |

LCD Menu

Figure 7-1 shows the LCD menu hierarchy. For parameter settings, see Table 3-4.

LCD menu hierarchy

Acronyms and Abbreviations

| A |  |
| --- | --- |
| AC | alternating current |
| ACDB | alternating current distribution box |
| B |  |
| BLVD | battery low voltage disconnection |
| C |  |
| CE | European Conformity |
| CISPR | International Special Committee on Radio Interference |
| CS | conducted susceptibility |
| D |  |
| D.G. | diesel generator |
| DC | direct current |
| E |  |
| EMC | electromagnetic compatibility |
| ESD | electrostatic discharge |
| I |  |
| IEC | International Electrotechnical Commission |
| L |  |
| LCD | liquid crystal display |
| LLVD | load low voltage disconnection |
| M |  |
| MTBF | mean time between failures |
| P |  |
| PE | protective earth |
| PMI | preventive maintenance inspection |
| PTP | point to point |
| R |  |
| RE | radiated emission |
| RH | relative humidity |
| RS | radiated susceptibility |
| S |  |
| SMU | site monitoring unit |
| T |  |
| TUV | Technical Watch-Over Association |